This SOP applies to all staff employed by NHS Greater Glasgow & Clyde and locum staff on fixed term contracts and volunteer staff.

##### SOP Objective

To minimise the risk of Pseudomonas aeruginosa infection in healthcare premises from water.

Document Control Summary

| Approved by and date | Board Water Safety Group, NHS GGC |
| --- | --- |
| Date of Publication | April 2015 |
| Developed by | IPCT |
| Related Documents | Standard Infection Control Precautions (SICPs) - (NIPCM) |
| Distribution/Availability | NHSGGC Infection Prevention and Control web page www.nhsggc.org.uk/infectioncontrol |
| Lead Manager | Board Infection Control Manager |
| Responsible Director | Board Medical Director |

Contents

- Introduction ................................................................................................ 4

- Critical control 2 ......................................................................................... 4

- Critical control 3-4 ...................................................................................... 5

- Critical control 5  ........................................................................................ 5

- Critical control 6 ......................................................................................... 5

- References  ................................................................................................. 5

- Appenidix 1  ................................................................................................ 6

- Appendix 2 .................................................................................................. 9

# Introduction

This SOP provides direction and guidance for ward based staff to meet their responsibilities as stated in HPS(2014) Guidance for neonatal units (NNUs) (levels 1,2&3), adult and paediatric intensive care units (ICUs) in Scotland to minimise the risk of Pseudomonas aeruginosa infection from water.  This document refers to critical control points 2 – 4 (inclusive) only.  (Critical points 1, 5 and 6 are considered in the NHSGGC Water Safety Policy and Written Scheme 2016).

*All wards / departments listed in the risk assessment for additional control measures to minimise the risk of Pseudomonas aeruginosa infection from water should be included in this guidance.

# Responsibilities

Senior Charge Nurses (SCNs) must:

- Follow this SOP.

- Undertake flushing of taps on clinical hand wash basins in clinical areas on days when the Facilities exception reports highlight that daily cleaning of those sinks has not been possible.

- Keep records of flushing of these taps for at least one month.

- Inform a member of the local Estates Team if this SOP cannot be followed in relation to flushing water outlets.

- Inform a member of the local Estates Team of infrequently used outlets which could be removed.

- Allow members of the local Estates Team access to complete maintenance as appropriate.

Estates must:

- Undertake actions deemed the responsibility of the local Estates Department as per the Water Safety Policy and Written Scheme.

- Keep a record of outlets reported that are deemed to be infrequently used and actions taken by them to remove this risk.

- Provide a report of maintenance actions and issues/ anomalies to the Sector Water Safety Group.

- Support staff locally to undertake their responsibilities in terms of reducing risk associated with pseudomonas.

Managers must:

- Make this SOP available to their staff.

- Support SCNs in following this SOP.

Board Water Systems Safety Group must:

- Keep this SOP up-to-date.

- Audit compliance with this SOP.

- Provide guidance via the Water Systems Safety Policy.

# 2. Critical Point 2:  Flushing Water Outlets to reduce the risk of Pipework System Contamination

Flushing of water outlets is necessary to control the build-up of biofilm in water systems to reduce the risk of transmission of pathogens via the environment and equipment to patients.

The Senior Charge Nurse (SCN) in each unit has responsibility (under current guidance) to ensure that the following recommendations are complied with in their area.  The SCN should ensure that:

  - All water outlets are flushed in high-risk environments daily, first thing in am for 
       1 minute at full flow (but not so that splashing goes beyond the basin).  This must 
       be recorded. In practice this will be assigned to the Facilities department as part 
       of the local cleaning schedule. Where this has not been possible e.g. access    
       issues,  then the flushing will be carried out by the SCN and a record kept (See 
        Appendix 2).

  - Any problems or concerns relating to the safety, maintenance, reduced usage,

any changes in use and cleanliness of all water outlets are identified and

reported to the ICT and the Estates Department as relevant.

# Critical Points 3 -4

The check list at Appendix 1 should be used by the SCN as a guide and assessment tool to provide assurance that risks from contamination by P. aeruginosa are managed as far as possible by ward staff in high risk areas.

Where units do not meet the guidance, an action plan should be developed to remedy any risks identified through this process.

All high risk areas in NHS GGC will be subject to 6 monthly water sampling for PA as per regime outlined in Appendix 3

# Critical Control Point 5: Surveillance and preparedness

IPCTs will:

- Include Pseudomonas aeruginosa from blood culture as an alert organism from all in-patient areas and from all specimens from ICUs, NICUs, PICUs and transplant units.

- Liaise with microbiology if further water testing required (e.g. suspected / confirmed outbreak)

Clinical Managers will:

- Support IPCT to undertake an assessment of the patients and ward

- Have a contingency plan for NICUs, PICU and ICUs to continue safe patient care without use of tap water, if identified a source.

# Critical Control Point 6: Investigation and control measures for clinical incidents

Where alert surveillance identifies  Pseudomonas aeruginosa bacteraemia in one of the adult high risk areas, or in any specimen from NICUs and PICU, the IPCT will undertake immediate assessment to determine if this is healthcare associated. Consideration should be given to:  previous colonisation / infection with PA; review of patient’s care; possible reservoirs in the clinical area and all relevant microbiology results.  The following action should be undertaken: 

1 isolate of PA in a high risk unit: The IPCT will undertake an audit using the PA Ward Audit Checklist (Appendix 1). If no issues, then no further action. If actions required , liaison with SCN to support remedial action. Summarise actions in SBAR for IPCT and SCN.

2 isolates of PA in 2 patients in 2 weeks

The IPCT will undertake an audit using the PA Ward Audit Checklist (Appendix 1). An incident  meeting will be arranged with IPCT, clinical team and relevant staff, including estates and or microbiology to agree investigation and action required.  Minutes should be kept and the incident summarised in an SBAR for IPCT and Sector Management Team.

# References

HPS (2014) Guidance for neonatal units (NNUs) (levels 1,2 &3), adult and paediatric intensive care units (ICUs) in Scotland to minimise the risk of Pseudomonas aeruginosa from water.

# Appendix 1: 	PA Ward Audit Checklist / Assessment Tool:

| Critical Control Point 3: Preventing Direct Water Usage Colonising / Infecting Vulnerable Patients | Requirement met Yes/No | Actions required/ completed |
| --- | --- | --- |
| 1.1 | Washing Babies: Babies are washed using clean, fresh tap water. |  |  |
| 1.2 | Defrosting Breast Milk: Breast milk is defrosted either: in a designated milk fridge outside fridge at room temperature OR using a warming/ defrosting device designed to ensure no direct contact with the bottle/ syringe with non-sterile water. Using sterile water warmed in a warming cabinet NB: Discard any milk not used once defrosted DO NOT USE WARM TAP WATER |  |  |
| 1.3 | Warming Breast/ Formula Milk: Milk is taken out of fridge one hour prior to use OR Milk is warmed using a warming device designed to ensure no direct contact with the bottle/ syringe with non-sterile water. Use warmed, sterile water |  |  |
| 1.4 | Use of Ice: Ice is not used for direct baby care in NNUs (all levels). Ice for consumption by severely immunocompromised patients should be made with sterile water. |  |  |

| Critical Control Point 4: Preventing Indirect Contact with P. aeruginosa from Colonised/ Infected Patients | Requirement met Yes/No |  |
| --- | --- | --- |
| 2.1 | Hand Wash Stations: Clinical hand wash sinks are used for hand washing only. Clinical Hand wash sinks are cleaned at least daily as per national Cleaning Specification. Hand hygiene product bottles are never topped up |  |  |
| 2.2 | Aseptic Procedures: Aseptic procedures are prepared and/ or performed in an area where there are no concurrent procedures being undertaken that generate splashing which could contaminate a sterile surface. Decontaminate all surfaces aseptic procedure surfaces with a detergent or alcohl wipe |  |  |
| 2.3 | Aerosol Generating Procedures: Existing guidance for aerosol generating procedures is followed. |  |  |
| 2.4 | Discarding Potentially Contaminated Fluids: Small volumes of fluid, e.g. ET/ ventilator condensate, are discarded into clinical waste bags. Larger volumes, e.g. bath water etc, are safely transported to a sink (not a hand wash sink) or sluice. |  |  |

| Critical Control Point 4: Preventing Indirect Contact with P. aeruginosa from Colonised/ Infected Patients | Requirement met Yes/No |  |
| --- | --- | --- |
| 2.5 | Suction/ Chest Drain Bottles: Disposable suction container liners are sealed and discarded in a suitable container or solidifying gel is used prior to discarding in healthcare waste. |  |  |
| 2.6 | Equipment Decontamination: All re-usable equipment is thoroughly dried following decontamination. |  |  |
| 2.7 | Humidifiers: Humidifiers on incubators: Only sterile or distilled water is used to fill and top up. Re-usable humidifiers are decontaminated in a Central Decontamination unit (CDU). |  |  |
| 2.8 | Storage of Equipment: Patient equipment is not stored where they may be exposed to splash contamination. |  |  |
| 2.9 | Non-Clinical Procedures that Create a Spray: Spray bottles are not used where possible. Spray bottles used for cleaning are not topped up. Spray bottles are not used in areas where aseptic procedures are being prepared or are ongoing. |  |  |

# Appendix 2:  Example of Flushing Record

DAILY FLUSHING OF WATER OUTLETS

| ROOM NUMBER/ BED SPACE | DATE | SIGNATURE |
| --- | --- | --- |

Appendix 3: Water testing protocol for Pseudomonas aeruginosa in NICU

Water outlets should be sampled 6-monthly

Water outlets which should be sampled include those with supply water that have:

- direct contact with patients

- used to wash staff hands before and after clinical procedures

- used to clean equipment that will have contact with patients

* 	Remedial measures

Consider the following:

- Continue daily flushing while out of use

- If practical consider removal of flow straighteners

- Hand washing should be supplemented by the use of alcohol gel

- Check unit for little-used outlets and if possible remove

- Check pipework for deadlegs and blind ends

- Consider disinfection e.g. chlorine dioxide

- Consider replacement taps

- Ensure best practice in relation to handwash basins

- Use bottled water for baby bathing until re-test –ve

Interpreting pre and post flush counts

High counts pre-flush (> 10 cfu/100ml) and low post flush (<10cfu/100ml) suggests local water outlet problem.

High count pre and post flush (> 10cfu/100ml) suggests wider problem with the water supply.  In this situation most outlets are likely to be positive and other points in the water system should be sampled.

# Text boxes

Water Sample

(Pre-flush)

>10 cfu/100ml

1-10 cfu/100ml

Not detected

Remove outlet from service and re-test pre/post flush

Re-test    pre/post flush

No further action

* Remediation (see below)

NEGATIVE: re-sample after 6 months or on advice of IPCT

Re-test in 3 days if positive remediation

If negative, re-instate and test at 2 and 4 weeks

Re-sample in 6 months or on advice of IPCT