**Guidance for ICDs for interpretation and management of hydropool results**

Sampling should take place weekly. One clear sample is sufficient to put the pool back into use.

*Hydropool Locations*

|  |  |
| --- | --- |
| SITE | LOCATION |
| QEUH | Room 11A, Ward 2A |
| QEUH | Block DA Spinal Injuries Unit |
| RAH | Ground Floor, REH-047, Physio Dept |
| GRI | Block BH Ground Floor Physio Disc 831 |
| IRH | Physiotherapy, Level C |

|  |  |  |  |
| --- | --- | --- | --- |
| Hazard | Result | Interpretation | Action |
| E Coli | >0 in 100 ml0 in 100 ml | UNSATISFACTORYSATISFACTORY | Investigate immediately. Take pool out of use, disinfect and repeat. |
| Coliforms | >10 in 100ml1-<10 in 100ml0 in 100 ml | UNSATISFACTORYACCEPTABLESATISFACTORY | Investigate immediately . Take pool out of use , disinfect and repeat.If positive on next weekly sample, take out of use, disinfect and repeat |
| Pseudomonas aeurginosa | >10 in 100 ml1-10 in 100ml | UNSATISFACTORYBORDERLINE | Investigate immediately. Take pool out of use, disinfect and repeat.Immediate resample and if positive action as above |
| Aerobic colony count | 0-<10ml>10-<100/ml>100ml | SATISFACTORYBORDERLINEUNSATISFACTORY | Repeat sample . If remains positive ask lab to identify organism. Take pool out of use, disinfect and repeat.Investigate immediately . Take pool out of use , disinfect and repeat |

References : 1) Examining food, water and environmental samples from healthcare environments. Public Health England Guidance 2013.